# SECTION 13 21 48

# MODULAR ENGINE DYNO TEST CELL

# WITH BLAST RELIEF PANELS

# PART 1 – GENERAL

# 1.1	SUMMARY

- Modular Engine Dyno Test Cell consisting of walls, ceiling, structural framing (as required), connecting members, doors, windows, exhaust plenum with blower/motor assembly, inlet and exhaust silencers, miscellaneous materials and all fasteners necessary to construct the Test Cell. The Modular Engine Dyno Test Cell is to be field assembled from 4” thick pre-manufactured components.  Enclosure is designed to meet performance criteria specified herein as a complete assembly.

- Provide labor, material, tools, equipment, scaffolding, transportation, inspection, certificates, and temporary protection necessary to:

- Provide Modular Engine Dyno Test Cell as shown on Drawings and as specified in these Specifications.  Provide accessories and appurtenances required for complete working installation.

- Connectors and flashing shall make holes in walls acoustically tight in accordance with Enclosure wall manufacturer’s instructions.

- Structural steel support frame, if required, by Engine Test Cell supplier.

- All electrical by others, refer to drawings.

- All ductwork between host building and test cell for air intake and air exhaust by others, refer to drawings.

# 1.2	QUALITY ASSURANCE:

- Regulatory Requirements:

- Acoustical performance: Minimum NRC (Noise Reduction Coefficient) rating of 1.00 and minimum STC (Sound Transmission Class) of 50 or 42 (refer to drawings for STC requirement) after panel fabrication.

- Structural Requirements: Design structure to support 30psf dead load. Modular Noise Control Room should be able to support men walking on it but it is not designed for storage unless shown on drawings.

- Reference Standards

- ASTM E90-99 or ASTM E90-02 and E413-87 Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions.

- ASTM C423-90A and ASTM E795-00, Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method.

# 1.3	SUBMITTALS:

- Product Data: Manufacturer's product specifications.

- Shop Drawings: Complete drawings showing components including mechanical and electrical requirements.

- Certificate of Compliance: Certify completed assembly meets requirements specified herein.

- Submit in accordance with Section 01300.

- Stamped (P.E.) calculations for all structural and panel components certifying compliance with roof and /or wind load requirements and California Seismic Zone Requirements (if applicable).

# 1.4	DELIVERY, STORAGE AND HANDLING

- Deliver products in sufficient quantity and time to maintain approved construction schedule.

- Materials shall be in original containers with seals unbroken and labels intact until time of use.  Wrapped or bundled materials shall bear name of manufacturer and product.  Damaged or otherwise unsuitable material, when so ascertained, shall be removed from Project site.

- Store products in secure, dry location, out of way of construction operations.  Store products off ground and protect from elements.  Wetting of elements not permitted.

- Prevent damage to materials, to other stored products, to existing construction, and project work.

# WARRANTY

Finish warranty: Furnish panel manufacturer's written warranty covering failure of the factory-applied finish on metal panels within the warranty period.  This warranty shall be in addition to and not a limitation of other rights the Owner may have against the Contractor under the Contract Documents.

# Warranty Period:  5 years

# 1.6	ACOUSTICAL PERFORMANCE GUARANTEE:

# Provide written guarantee that the assembled Test Cell will provide a minimum of 35 dBA noise reduction when measured three feet from walls, windows, doors,  intake and exhaust silencer openings. If Test Cell does not achieve the minimum noise reduction performance the Test Cell supplier is responsible for taking corrective action and the supplier’s expense to bring the assembled Test Cell into compliance with Acoustic Performance Guarantee.

# 1.7	EXPERIENCE:

# Test Cell supplier must provide a list of twenty (20) similar successful installations of Modular Engine Test Cells supplied within the last five years.

# PART 2 – PRODUCTS

# 2.1 	MATERIALS

Modular Engine Dyno Test Cell shall be constructed of type “QuietMod” H/P 42 and/or H/P 50 Panels, STC 52 Door Panels, and Window Panels manufactured by Noise Barriers.

Manufacturer:

Noise Barriers						Phone:  (847) 843-0500

Fax:      (847) 843-0501

www.noisebarriers.com

Contact:

John Finnegan					Phone:	 (315) 682-3821

Email:  info@noisebarriers.com                                Fax:	 (315) 682-3868

2.2	PANEL CONSTRUCTION

- Except as shown on Drawings or at locations described below, use 2” thick or 4” thick acoustical panels. Exterior surfaces are solid sheet 16-ga. Galvanized steel. Interior surfaces are 22 ga. Perforated galvanized steel.

- Sound-retarding and absorbing fill material shall be noncombustible, inert mildew-resistant and vermin proof.

- Lateral panel reinforcement, if required, shall be minimum of 18 ga. Cold rolled steel and spaced so vertical span does not exceed 2 ft. – o in.

- Spot welds shall be no more than 2 in. apart.

- Prior to attaching face sheet, panel shall be dampened and filled with sound-retarding and absorbing elements.  Fill shall be slightly larger and thicker than inside dimensions of panel.  No voids will be tolerated.

- Weld and rivet face sheet to panel assembly to acoustically compress and hold fill materials in place.  Panel assembly shall hold fill materials in place under severe conditions of vibration encountered in shipping, installation, and in operation of completed structure.

- Acoustic fill material shall be protected by means of a Tape-sealed bag.  Bagged fill shall be held back from inside perforated surface by means of an open mesh spacer.

- Weep holes to permit water runoff shall be provided on all horizontal surfaces.

  - DOOR PANELS

- Door leaf shall be STC 52, 2.5 inches thick fabricated from minimum 12 gauge and 16 gauge steel and filled with sound absorbing and damping elements with a clear opening as shown on the drawings.

- Frame shall be fabricated from 14 gauge steel.

- Assembly and adjustment of single leaf door, frame, acoustic seals and hinges shall take place at the factory and the entire unit shall ship to the jobsite ready for installation and operation.  All doors shall be tested for proper operation in the factory prior to shipment.

- Acoustic Seals:  Sides and head of door and frame shall receive two (2) sets of self-aligning magnetic-compression seals.  Door to be held in place by magnetic force of perimeter seals.  Acoustic labyrinth shall be created when door is in closed position.  Bottom of door leaf shall contain continuous gravity activated seal, which shall compress against floor as door is closed.  Raised sills and threshold drop seals will not be permitted.

- Hardware:

    - Hinges – minimum of two (2) Cam-Lift hinges finished in US 26-D satin chrome shall be supplied with each door leaf.

    - Latches shall not e required to hold the door closed or to achieve acoustic seal.

    - Pull handles, inside and outside, shall be supplied and installed at the factory.

    - Double leaf door sets shall include a Dorma Modified Model TS93GSRCONTSN4689 Coordinator.

  - WINDOW PANELS

- Windows shall be furnished in panels of the type and construction specified as shown on the drawings and panel schedule.

- Windows shall consist of two (2) layers (one layer ½” thick, the other layer 3/8” thick) safety glass separated by an air space and sealed in acoustically tight rubber seals.

- Air space shall contain a desiccant material to prevent fogging.

2.5	PANEL JOINERS AND CONNECTORS

- Construct connecting panel joiners of galvanized steel.  Joiner design and fit shall prevent noise leakage while acoustically and structurally joining panels together. Joiners shall be roll formed sections independent of basic panel so there is no possibility of direct passage of noise.

- Joiners and connectors shall be detailed to support loads shown on Drawings.

- Weep holes to permit water runoff shall be provided on all horizontal surfaces that may trap water.

2.6	FINISH PAINT and PACKAGING

- Manufacturer's high performance Polyester Powder Paint coating for applications to meet warranty requirements.

- Apply coatings before, during, or after forming and fabricating panels, as required by coating process and as required for maximum coating performance capability.  Fully coat all edges of perforations in face sheet.  Protect coating either by application of strippable film or by packing plastic film or other suitable material between panels to protect the finish during shipment.  Provide air-drying spray finish in matching color for touch up.

Color: Architect will select from manufacturer’s standard color chart.

- Provide sufficient paint to touch-up panels after installation of t.

- All materials shall be shipped in covered wooden crates.

2.7	INTERCHANGEBILITY AND REUSE

- Acoustic structural components having same part numbers shall be completely interchangeable.

- Acoustic structure shall be such that no components will be damaged upon disassembly.  Design shall allow structure to be assembled, disassembled and reassembled minimum of 3 times without detraction from acoustic performance.

2.8	PRESSURE RELIEF FASTENERS

A.	Mechanical fastener system designed to fail by tension when panel is subjected to an internal pressure of 25 lbs. per sq. ft., allowing the wall panel to blow-out and relieve the internal pressure.

2.9	DISSIMILAR MATERIALS ISOLATION

- Where aluminum comes in contact with other materials and metals, insulate the contact surfaces of aluminum.  Use aluminum bituminous coating, brushable non-hardening butyl coating, insulating tape or other system standard with the panel manufacturer and approved by the Owner’s Representative.

2.10 PANEL COMPONENT CHARACTERISTICS

- Submit certified Acoustical Testing laboratory test reports including absorption and transmission loss values for specified panel type and construction of not less than following:

Sound Transmission Loss, dB

OCTAVE BAND

Center Frequencies, HZ 		125	250	500	1K	2K	4K	STC

H/P 42   4” thick			23	31	40	49	56	62	42

H/P 50   4” thick			29	37	48	56	57	54	50

Sound Absorption Coefficients

OCTAVE BAND

Center Frequencies, HZ  		125	250	500	1K	2K	4K	NRC

H/P 42   4” thick			0.68	1.06	1.12	1.08	1.03	0.98	0.95

H/P 50   4” thick			0.41	0.95	1.23	1.03	1.01	1.01	1.05

B:  Submit certified Fire Testing Laboratory test reports including Flame Spread Index (FSI) and Smoke Developed Index (SDI) values for specified panel type and construction of not less than following:

STC 42 Panel Construction: 		FSI 0.00 	SDI 0.45

STC 50 Panel Construction: 		FSI 0.00 	SDI 0.16

III.    PART 3 - EXECUTION

3.1	STRUCTURAL STEEL FRAME (if applicable)

- Install columns, roof beams and structural panel support members and anchorage in accordance with AISC Manual of Steel Construction "Code of Standard Practice".

- Install panel support members on concrete floor of host building using methods and materials recommended by Test Cell manufacturer.

  - PANEL INSTALLATION

- Install panels according to manufacturer's instructions and recommendations, as applicable to project conditions and supporting substrates.  Anchor panels and other components of the work securely in place, with provisions for thermal and structural movement.

- Field cutting of exterior panels is not permitted.

- Install panels with exposed fasteners pre-finished to match panel finishes.

- Accessories:  Install components required for a complete acoustical enclosure panel system, including trim, coping, supports and attachments, connections between panels, seam covers, sealants, fillers, closures strips and similar items.

- Pressure Release Fastening:

  - Where pressure release fastening for wall panels are shown, arrange panels and secure with pressure release fastener system per Owner’s Underwriter’s requirement so panels will release at 25 lbs. per sq. ft. of pressure.

  - Provide safety chains, secured to siding and to structural supports, of sufficient length and strength to allow siding to be released but to restrict its outward travel from dropping more than 1 foot away from the building.

  - CLEANING AND ADJUSTMENT

- Damaged units:  Replace panels and other components of the work that have been damaged or have deteriorated beyond successful repair by means of finish touch up or similar minor repair procedures.

- Cleaning: Remove temporary protective coverings and strippable films (if any) as soon as each panel is installed. Upon completion of panel installation, clean finished surfaces as recommended by panel manufacturer, and maintain in a clean condition during construction.

## END OF SECTION